# ARCHITECTURAL CEILING HANGERS SPECIFICATION

30NCC, W30N, W30NCC

Ceiling Hangers shall be fail safe and include a steel frame containing an AASHTO Bridge Bearing Quality LDS Rubber Element at the top and a nominal 1” deflection steel spring at the bottom. Springs shall be seated in an LDS cup with a rubber bushing extending through the box to prevent metal to metal contact between the steel suspension rod and the frame. Dynamic Stiffness of Cup and Element shall not exceed 1.4. The ID of the bushing must allow a 30° swing from side to side before rod contact. Springs shall be factory precompressed to 70% of the assigned deflection. Hangers shall be Mason Industries 30NCC for 11/2 x 1/2 channel, W30N for wire, or W30NCC for wire and channel. Submittals shall confirm AASHTO Quality and Dynamic Stiffness in addition to deflection.

30CC, W30, W30CC

Ceiling Hangers shall be fail safe and include a steel frame containing a nominal 1” deflection steel spring seated in an AASHTO Bridge Bearing Quality Low Dynamic Stiffness Rubber Cup with a rubber bushing extending through the box to prevent metal to metal contact between the steel suspension rod and the frame. Dynamic Stiffness of the cup shall not exceed 1.4. The ID of the bushing must allow a 30° swing from side to side before rod contact. Springs shall be factory precompressed to 70% of the assigned deflection. Hangers shall be Mason Industries 30CC for 11/2 x 1/2 channel, W30 for wire, W30CC for wire and 11/2 x 1/2 channel. Submittals shall confirm AASHTO Quality and Dynamic Stiffness in addition to deflection.

30CSCH

Ceiling Hangers shall have a steel frame formed to minimize height by supporting 11/2 x 1/2 ceiling channels on either side of a 1” nominal deflection centered spring. The spring shall be seated in an AASHTO Bridge Bearing Quality LDS Rubber Cup with a rubber bushing extending through the frame to prevent metal to metal contact between the steel suspension rod and the frame. Rubber Dynamic Stiffness shall not exceed 1.4. The ID of the bushing must allow a 30° swing from side to side before rod contact. Springs shall be factory precompressed to 70% of the assigned deflection. Hangers shall be Mason Industries 30CSCH. Submittals shall confirm AASHTO Quality and Dynamic Stiffness in addition to deflection.

W30SM, 30SMCC

Ceiling Hangers shall consist of a side attachment steel angle gusseted on each side to prevent bending. The gussets shall protect a 1” nominal deflection steel spring seated in a Bridge Bearing Quality LDS Rubber Cup with a rubber bushing extending through the horizontal leg to prevent metal to metal contact between the steel suspension rod and the frame. Rubber Dynamic Stiffness shall not exceed 1.4. The ID of the bushing must allow a 30° swing from side to side before rod contact. Springs shall be factory precompressed to 70% of the assigned deflection. Hangers shall be Mason Industries W30SM for ceiling wire attachment or 30SMCC if 11/2 x 1/2 ceiling channels are used. Submittals shall confirm AASHTO Quality and Dynamic Stiffness in addition to spring deflection.

HDCC, WHD, WHDCC

Ceiling Hangers shall be fail safe and include a steel frame containing an AASHTO Bridge Bearing Quality LDS Rubber Element molded with an integral lock in grommet at the bottom to prevent steel rod to housing contact. Dynamic Stiffness shall not exceed 1.4 nor the corrected frequency 8 Hz. Housing configurations shall be offered to accommodate bolting to structure and simple attachment to 11/2 x 1/2 channel, 12 gauge wire top and bottom or 12 gauge wire on top and 11/2 x 1/2 channel on the bottom. Ceiling hangers shall be Mason Industries type HDCC, WHD or WHDCC as required. Submittals shall confirm AASHTO Quality and Dynamic Stiffness in addition to frequency.

WHR

Ceiling Hangers shall be fail safe and consist of opposed washers sandwiching an AASHTO Bridge Bearing Quality LDS Rubber Element 11/8” thick. Dynamic Stiffness shall not exceed 1.4” nor the corrected frequency 12 Hz. Connections shall be made with 12 gauge wire top and bottom passing through hairpin loops attached to the opposing washers. Ceiling Hangers shall be Mason Industries type WHR. Submittals shall confirm AASHTO Quality and Dynamic Stiffness in addition to frequency.

CRCH

Ceiling Hangers shall have a steel frame formed to minimize height by holding an 11/2 x 1/2 ceiling channel on either side of an AASHTO Bridge Bearing Quality LDS Rubber Element molded with an integral lock in grommet at the bottom to prevent steel rod to housing contact. Dynamic Stiffness shall not exceed 1.4 nor the corrected frequency 8 Hz. Ceiling Hangers shall be Mason Industries CRCH. Submittals shall confirm AASHTO Quality and Dynamic Stiffness in addition to frequency.

HDSMCC, WHDSM

Ceiling Hangers shall consist of a side attachment steel angle gusseted on each side to prevent bending. The gussets shall protect an AASHTO Bridge Bearing Quality LDS Rubber Element molded with an integral lock in grommet at the bottom to prevent steel rod to housing acoustical short circuiting. Dynamic Stiffness shall not exceed 1.4 nor the corrected frequency 8 Hz. Housing configurations shall be offered for simple attachment to 11/2 x 1/2 channels or 12 gauge wire. Ceiling Hangers shall be Mason Industries HDSMCC or WHDSM. Submittals shall confirm AASHTO Quality and Dynamic Stiffness in addition to frequency.