# JACK-UP SYSTEM SPECIFICATION

LDS JACK-UP SYSTEM FOR MECHANICAL EQUIPMENT ROOMS WITH MACHINERY SUPPORTED BY THE FLOATING FLOOR.

GENERAL

SCOPE

- Isolate floating floors from building structure by means of jack-up LDS isolators and perimeter isolation in each of the mechanical equipment rooms as shown on the drawings.

If sound barrier walls are used, add the following:

- Build sound barrier walls on the floating floors.

SUBSTITUTION OF MATERIALS

Substitute materials shall meet or exceed the “quality” of the products which are listed in these Specifications. Submit samples and test reports by an independent laboratory for consideration on this project.

INTENT

- The floating floor system shall consist of a 4” (100mm) thick concrete slab isolated from and supported 2” (50mm) above the waterproofed structural slab by resilient LDS isolators within cast iron housings designed to jack up the floor after pouring on the sub-floor.

If sound barrier walls are used, add the following:

Sound barrier walls consisting of 6” (150mm) filled concrete block (Barrier wall construction can be changed when writing specification) shall rest on the floating floor with a 31/2” air gap to the structural walls. (31/2” (90mm) may be reduced to 2” (50mm) if no sway braces are needed.)

- The floating floor slab shall be isolated from adjoining walls, columns and curbs by means of perimeter isolation.

- Any floor drains, piping, conduit and duct penetrations must not short circuit the isolation system.

- Any equipment within these rooms shall be mounted on housekeeping pads or directly on the floating floor as shown on the drawings.

- In seismic zones the floating floor shall be restrained horizontally by curbs or walls designed to withstand the horizontal seismic forces. Solid bridge bearing LDS pads shall be interspersed between perimeter isolation to withstand the seismic forces with a maximum deflection of 0.2” (5mm). When perimeter cannot be used for seismic constraint, intersperse horizontal restraints within floor system.

- In seismic zones 2, 3 and 4 or equivalent Av, the floor shall be protected by embedded double acting resilient floor snubbers set in opposition to the overturning moments at the equipment snubbers in all locations where the center of gravity of major equipment is high.

PERDORMANCE REQUIREMENTS

- The floating floor system shall have a minimum rating of STC-79 and INR+17 as verified by an independent laboratory in prior tests.

FLOOR SYSTEM CONSTRUCTION PROCEDURE

- The setting of all isolation materials and raising of the floor shall be performed by or under the supervision of the isolation manufacturer.

- Set and waterproof any drains and lower pipe seals in keeping with waterproofing specifications.

- Cement perimeter isolation around all walls, columns, curbs, etc.

  - In seismic zones intersperse the perimeter isolation with bridge bearing quality LDS pads the thickness of the perimeter isolation or bolt to the sub-floor.

- Cover entire floor area with 6 mil (0.15mm) plastic sheeting and carry sheeting up perimeter isolation.

- Place bell-shaped castings on a maximum of 54” (1370mm) centers in the general areas in strict accordance with the approved drawings prepared by the isolation manufacturer. Spacing can be increased to straddle machinery locations. Additional reinforcement must be detailed on isolation manufacturer’s drawings when required. If sound barrier walls are used, add the following: Perimeter isolators shall be selected to support the wall weight in addition to the perimeter of the floating floor.

  - In seismic zones attach double acting resilient seismic snubbers to the structural slab on either side of high center of gravity equipment to withstand the overturning moment generated by the machinery snubbers and prevent failure of the floating floor.

- Place reinforcing as shown on the drawings and pour floor monolithically.

- Raise floor 2” (50mm) by means of the jack-screws. (If construction sequence dictates raising the floor before placing machinery, heavy planking must be used to protect floor while machinery is being rolled into position).

- Caulk perimeter isolation in all locations and grout jack-screw holes.

If sound barrier walls are used, add the following:

- Construct block walls on the floating floor being careful that mortar does not drop behind the walls. Place 2”(50mm) fiberglass bats against the structural wall as a precaution. Provide sway braces and isolated angle iron wall braces at the top of the walls. Caulk angle iron braces.

- In seismic zones adjust the double acting snubbers after machinery is in place to provide a maximum up and down clearance of 0.125” (3mm).

SUBMITTALS

- Detailed product drawings and Load/Deflection curves of all isolators, double acting floor snubbers and/or other snubbing restraints when required.

- AASHTO Test Reports on all properties in table 2.01 A from an accredited independent laboratory for all rubber durometers used

- Dynamic stiffness test from an accredited independent laboratory at 5, 10 and 15 Hz, showing dynamic stiffness does not exceed 1.4.

  - Isolation frequency not to exceed 9 Hz at stated deflection.

- Acoustical test data from an independent laboratory showing a minimum STC of 79 and a minimum INR of 17 using a 4” (100mm) concrete floating floor, a 6” (152mm) structural floor and a 2” (50mm) air gap.

- A drawing or drawings showing:

  - Dead, live and concentrated loads.

  - Isolator sizes, deflections, frequencies and locations and in seismic zones, locations of seismic snubbers. If sound barrier walls are used, add the following to b: Wall sway brace and isolated angle iron brace sizes, locations and frequencies.

  - Any drain and penetration locations.

  - Size, type, elevation and spacing of concrete reinforcement.

  - Caulking details.

  - Floor or floor and wall construction procedure.

QUALITY ASSURANCE

- Floating floor system components shall be designed and fabricated by a manufacturer with at least ten years experience in one hundred similar installations.

- The floating floor isolation materials shall be installed and the floor raised by or under the supervision of the isolator manufacturer.

SITE CONDITIONS

- If site conditions are unsatisfactory or raise questions about the installation of the floating floor, the work will not proceed until the condition has been corrected in a manner acceptable to the isolation manufacturer. The sub-floor must have the same pitch as the top of the floating floor or special provisions made for isolator housings of different height.

SEQUENCING AND SCHEDULING

- Coordinate work with other trades and coordinate scheduling with the construction supervisor to minimize delays.

PRODUCTS

ISOLATORS

- Bell shaped castings with integral lugs to locate reinforcing, shrouding 2” (50mm) thick LDS isolators molded to the following and all other AASHTO bridge bearing specifications. All housings shall have 3/4” (20mm) minimum diameter jackscrews. Deflections shall not exceed 0.3” (7.5mm) nor the frequency 9 Hz. Isolators shall be Mason Industries type FSN.

Table 1. AASHTO Bridge Bearing Specifications for polyisoprene

NOTE: 40 Durometer is not included in AASHTO Specifications. Numbers are Mason standard.

If sound barrier walls are used, add the following:

- In seismic zones double acting resilient cast in floating floor snubbers shall consist of a ductile iron housing locked into the floating floor. The housing shall have a removable cover plate to provide access to the adjustment of clearances in both the up and down directions of the resilient stops. Resilient stops shall be attached to a restraining bolt attached to the structural floor with an approved anchor. Double acting snubbers shall be Mason Industries Type SFFS.

- Wall Sway Braces: Double acting LDS sway braces with a fail-safe feature in three planes. Braces shall be furnished with a bracket for bolting to the structural wall and a hooked end for insertion in the masonry joint. Braces shall have a frequency not in excess of 10Hz based on the weight of the wall area per brace and a vertical stiffness not in excess of 50% of the horizontal. Sway Braces shall be Mason Industries Type DNSB.

- Angle Brackets: 11/2” (40mm) x 2” (50mm) angle iron sections with provision for bolting to the structure and a minimum thickness of 3/8” (9mm) sponge cemented to the vertical leg. Angle Brackets shall be Mason Industries AB-716.

BOND BREAKER MATERIAL

- Provide one (1) layer of 6 mil (0.15mm) polyethylene sheeting.

PERIMETER ISOLATION

- Minimum 3/4”(20mm) thick PVC foam, density 7 lbs/ft3 average. PVC foam shall be Mason Industries P7.

- In seismic zone perimeter isolation shall be interspersed with 3/4”(20mm) thick, 60 durometer LDS bridge bearing pads the height of the perimeter material. Bridge bearing pad shall be made to the same AASHTO specifications, as shown for the FSN mountings and sized for a maximum deflection of 0.2”(5mm) at maximum earthquake forces. Interspersed pads shall be Mason Industries Type LDS-BBP.

PERIMETER CAULKING COMPOUND

- Non-hardening, drying or bleeding. Troweling or pouring grade. Caulking compound shall be Mason Industries Type CC-75.

FLOATING FLOOR DRAINS

- Cast iron design. The upper funnel section cast into the floating floor. Lower bucket, built into the structure, shall retain water surrounding the upper section as a between floors sound seal. Weep holes are required to drain the structural floor. Floor drains shall have water proofing membrane clamps. Floor drains shall be Mason Industries Type CFD-18591.

EXECUTION

INSALLATION

- Install the floating floor systems according to the installation and adjustment procedures and drawings submitted by the isolator manufacturer and approved by the architect.

The following table is a general guide to floor thicknesses and air gaps. All specifications may be modified to your requirements.

# JACK-UP SYSTEM SPECIFICATION

LDS JACK-UP SYSTEM FOR TV Studios, Theatres, Bowling Alleys, Kitchens, Squash Courts, Exercise Rooms, etc.

GENERAL

We have left the blank below for you to fill in the name of the area, i.e. Auditorium, TV Studio, etc. Please specify floor finish such as hardwood or tile as you normally do in another section.

SCOPE

- Isolate floating floors from building structure by means of jack-up LDS isolators and perimeter isolation in each of the (fill in name of area) _____________________.

If sound barrier walls are used, add the following:

- Build sound barrier walls on the floating floors.

SUBSTITUTION OF MATERIALS

- Substitute materials shall meet or exceed the “quality” of the products which are listed in these Specifications. Submit samples and test reports by an independent laboratory for consideration on this project.

DESIGN

INTENT

- The floating floor system shall consist of a 4” (100mm) thick concrete slab isolated from and supported 2” (50mm) above the structural slab by resilient LDS isolators within cast iron housings designed to jack up the floor after pouring on the sub-floor. Sub floors shall be waterproofed under kitchens. If sound barrier walls are used, add the following: Sound barrier walls consisting of 6” (150mm) filled concrete block (Barrier wall construction can be changed when writing specification) shall rest on the floating floor with a 31/2” (90mm) air gap to the structural walls. (31/2” (90mm) may be reduced to 2” (50mm) if no sway braces are needed.)

- The floating floor slab shall be isolated from adjoining walls, columns and curbs by means of perimeter isolation.

- Any floor drains, piping, conduit and duct penetrations must not short circuit the isolation system.

- In seismic zones the floating floor shall be restrained horizontally by curbs or walls designed to withstand the horizontal seismic forces. Solid bridge bearing LDS pads shall be interspersed between perimeter isolation to withstand the seismic forces with a maximum deflection of 0.2” (5mm). When perimeter cannot be used for seismic constraint, intersperse horizontal restraints within floor system.

PERFORMANCE REQUIREMENTS

- The floating floor system shall have a minimum rating of STC-79 and INR+17 as verified by an independent laboratory in prior tests.

FLOOR SYSTEM CONSTRUCTION PROCEDURE

- The setting of all isolation materials and raising of the floor shall be performed by or under the supervision of the isolation manufacturer.

- Set and waterproof any drains and lower pipe seals in keeping with waterproofing specifications.

- Cement perimeter isolation around all walls, columns, curbs, etc.

  - In seismic zones intersperse the perimeter isolation with bridge bearing quality LDS pads the thickness of the perimeter isolation.

- Cover entire floor area with 6 mil (0.15mm) plastic sheeting and carry sheeting up perimeter isolation.

- Place bell-shaped castings on maximum 54” (1370mm) centers in the general areas in strict accordance with the approved drawings prepared by the isolation manufacturer. Additional reinforcement must be detailed on isolation manufacturer’s drawings when required. If sound barrier walls are used, add the following: Perimeter isolators shall be selected to support the wall weight in addition to the perimeter of the floating floor.

- Place reinforcing as shown on the drawings and pour floor monolithically.

- Raise floor 2” (50mm) by means of the jack-screws.

- Caulk perimeter isolation in all locations and grout jack-screw holes.

If sound barrier walls are used, add the following:

- Construct block walls on the floating floor being careful that mortar does not drop behind the walls. Place 2” (50mm) fiberglass bats against the structural wall as a precaution. Provide sway braces and isolated angle iron wall braces at the top of the walls. Caulk angle iron braces.

SUBMITTALS

- Detailed product drawings and Load/Deflection curves of all isolators.

- AASHTO Test Reports on all properties in table 2.01 A from an accredited independent laboratory for all rubber durometers used.

- Dynamic stiffness test from an accredited independent laboratory at 5, 10 and 15 Hz, showing dynamic stiffness does not exceed 1.4. 3a. Isolation frequency not to exceed 9 Hz at stated deflection.

- Acoustical test data from an independent laboratory showing a minimum STC of 79 and a minimum INR of 17 using a 4”(100mm) concrete floating floor, a 6”(150mm) structural floor and a 2”(50mm) air gap.

- A drawing or drawings showing:

  - Dead, live and concentrated loads.

  - Isolator sizes, deflections, frequencies and locations. If sound barrier walls are used, add: wall sway brace and isolated angle iron brace sizes, locations and frequencies.

  - Any drains or other penetrations.

  - Size, type, elevation and spacing of concrete reinforcement.

  - Caulking details.

  - Floating floor and wall construction procedure.

QUALITY ASSURANCE

- Floating floor system components shall be designed and fabricated by a manufacturer with at least ten years experience in one hundred similar installations.

- The floating floor isolation materials shall be installed and the floor raised by or under the supervision of the isolator manufacturer.

SITE CONDITIONS

- If site conditions are unsatisfactory or raise questions about the installation of the floating floor, the work will not proceed until the condition has been corrected in a manner acceptable to the isolation manufacturer. The sub-floor must have the same pitch as the top of the floating floor or special provisions made for isolator housings of different height

SEQUENCEING AND SCHEDULING

Coordinate work with other trades and coordinate scheduling with the construction supervisor to minimize delays.

PRODUCTS

ISOLATORS

- Bell shaped castings with integral lugs to locate reinforcing, shrouding 2” (50mm) thick LDS isolators molded to the following AASHTO bridge bearing specifications. All housings shall have 3/4” (20mm) minimum diameter jackscrews. Deflections shall not exceed 0.3” (7.5mm) nor the frequency 10Hz. Isolators shall be Mason Industries type FSN.

Table 1. AASHTO Bridge Bearing Specifications for polyisoprene

NOTE: 40 Durometer is not included in AASHTO Specifications. Numbers are Mason standard.

If sound barrier walls are used, add the following:

- Wall Sway Braces: Double acting LDS sway braces with a fail safe feature in three planes. Braces shall be furnished with a bracket for bolting to the structural wall and a hooked end for insertion in the masonry joint. Braces shall have a frequency not in excess of 10Hz based on the weight of the wall area per brace and a vertical stiffness not in excess of 50% of the horizontal. Sway braces shall be Mason Industries Type DNSB.

- Angle Brackets: 11/2”(40mm) x 2”(50mm) angle iron sections with provision for bolting to the structure and a minimum thickness of 3/8”(9mm) sponge cemented to the vertical leg. Angle Brackets shall be Mason Industries AB-716.

BOND BREAKER MATERIAL

- Provide one (1) layer of 6 mil (0.15mm) polyethylene sheeting.

PERIMETER ISOLATION

- Minimum 3/4”(20mm) thick PVC foam, density 7 lbs/ft3 average. PVC foam shall be Mason Industries P7.

- In seismic zone perimeter isolation shall be interspersed with 3/4”(20mm) thick, 60 durometer LDS bridge bearing pads the height of the perimeter material. Bridge bearing pad shall be made to the same AASHTO specifications, as shown for the FSN mountings and sized for a maximum deflection of 0.2”(5mm) at maximum earthquake forces. Interspersed pads shall be Mason Industries Type LDS-BBP.

PERIMETER CAULKING COMPOUND

- Non-hardening, drying or bleeding. Troweling or pouring grade. Caulking compound shall be Mason Industries Type CC-75.

FLOTING FLOOR DRAINS

- Cast iron design. The upper funnel section cast into the floating floor. Lower bucket, built into the structure, shall retain water surrounding the upper section as a between floors sound seal. Weep holes are required to drain the structural floor. Floor drains shall have water proofing membrane clamps. Floor drains shall be Mason Industries Type CFD-18591.

EXECUTION

INSTALLATION

- Install the floating floor systems according to the installation and adjustment procedures and drawings submitted by the isolator manufacturer and approved by the architect.

# JACK-UP SYSTEM SPECIFICATION

LDS JACK-UP SYSTEM FOR ROOFS

GENERAL

SCOPE

- isolation in each of the roof areas shown on the drawings.

If sound barrier walls are used, add the following:

- Build sound barrier walls on the floating floors.

SUBSTITUTION OF MATERIALS

- Substitute materials shall meet or exceed the “quality” of the products which are listed in these Specifications. Submit samples and test reports by an independent laboratory for consideration on this project.

DESIGN

INTENT

- The floating roof system shall consist of a 4” (100mm) waterproofed concrete slab isolated and supported 2” (50mm) above the waterproofed structural slab by resilient LDS isolators within cast iron housings designed to jack up the roof after pouring on the sub-roof. If sound barrier walls are used, add the following: Sound barrier walls consisting of 6” (150mm) filled concrete block (Barrier wall construction can be changed when writing specification) shall rest on the floating floor.

- The floating roof slab shall be isolated from adjoining walls, columns, and curbs by means of perimeter isolation.

- Any equipment mounted directly on the floating roof shall be installed so as not to damage the roof’s waterproofing.

- Flashing and waterproofing shall be completed after the roof is raised. Perimeter flashing shall allow for downward movement of 0.5” (12mm).

- In seismic zones the floating floor shall be restrained horizontally by curbs or walls designed to withstand the horizontal seismic forces. Solid bridge bearing LDS pads shall be interspersed between perimeter isolation to withstand the seismic forces with a maximum deflection of 0.2”(5mm). When perimeter cannot be used for seismic constraint, intersperse horizontal restraints within floor system.

- In seismic zones 2, 3 and 4 or equivalent Av, the roof shall be protected by embedded double acting resilient floor snubbers set in opposition to the overturning moments at the equipment snubbers in all locations where the center of gravity of major equipment is high.

PERFORMANCE REQUIREMENTS

- The floating roof system shall have a minimum rating of STC-79 and INR+17 as verified by an independent laboratory in prior tests.

ROOF SYSTEM CONSTRUCTION PROCEDURE

- The setting of all isolation materials and raising of the roof shall be performed by or under the supervision of the isolation manufacturer.

- Set and waterproof any drains and lower pipe seals in keeping with waterproofing specifications.

- Cement perimeter isolation around all walls, columns, curbs, etc.

  - In seismic zones intersperse the perimeter isolation with bridge bearing quality LDS pads the thickness of the perimeter isolation.

- Cover entire floor area with 6 mil (0.15mm) plastic sheeting and carry sheeting up perimeter isolation.

- Place bell-shaped castings on maximum 54”(1370mm) centers in the general areas in strict accordance with the approved drawings prepared by the isolation manufacturer. Spacing can be increased to straddle machinery locations. Additional reinforcement must be detailed on isolation manufacturer’s drawings when required. If sound barrier walls are used, add the following: Perimeter isolators shall be selected to support the wall weight in addition to the perimeter of the floating roof. 5a. In seismic zones attach double acting resilient seismic snubbers to the structural slab on either side of high center of gravity equipment to withstand the overturning moment generated by the machinery snubbers and prevent failure of the floating roof.

- Place reinforcing as shown on the drawings and pour roof monolithically.

- Raise roof 2”(50mm) by means of the jack-screws. (If constructions sequence dictates raising the roof before placing machinery, heavy planking must be used to protect the roof if machinery is rolled into position).

- Caulk perimeter isolation in all locations and grout jack-screw holes.

If sound barrier walls are used, add the following:

- Construct block walls on the floating floor being careful that mortar does not drop behind the walls. Place 2”(50mm) fiberglass bats against the structural wall as a precaution. Provide sway braces and isolated angle iron wall braces at the top of the walls. Caulk angle iron braces.

- In seismic zones adjust the double acting snubbers after machinery is in place to provide a maximum up and down clearance of 0.125”(3mm).

- Install waterproofing and flashing.

SUBMITTALS

- Detailed product drawings and Load/Deflection curves of all isolators and in seismic zones double acting floor snubbers.

- AASHTO Test Reports on all properties in table 2.01 A from an accredited independent laboratory for all rubber durometers used.

- Dynamic stiffness test from an accredited independent laboratory at 5, 10 and 15 Hz, showing dynamic stiffness does not exceed 1.4.

  - Isolation frequency not to exceed 9 Hz at stated deflection.

- Acoustical test data from an independent laboratory showing a minimum STC of 79 and a minimum INR of 17 using a 4”(100mm) concrete floating floor, a 6”(150mm) structural floor and a 2”(50mm) air gap.

- A drawing or drawings showing:

  - Dead, live and concentrated loads.

  - Isolator sizes, deflections, frequencies and locations and in seismic zones, locations of seismic snubbers.

  - Any drains or other penetrations.

  - Size, type, elevation and spacing of concrete reinforcement.

  - Caulking details.

  - Roof system construction procedure.

QUALITY ASSURANCE

- Floating roof system components shall be designed and fabricated by a manufacturer with at least ten years experience in one hundred similar floor or roof installations.

- The floating roof isolation materials shall be installed and the roof raised by or under the supervision of the isolator manufacturer

SITE CONDITIONS

- If site conditions are unsatisfactory or raise questions about the installation of the floating roof, the work will not proceed until the condition has been corrected in a manner acceptable to the isolation manufacturer. The sub-roof must have the same pitch as the top of the floating roof or special provisions made for isolator housings of different height.

SEQUENCING AND SCHEDULING

- Coordinate work with other trades and coordinate scheduling with the construction supervisor to minimize delays.

PRODUCTS

ISOLATORS

- Bell shaped castings with integral lugs to locate reinforcing, shrouding 2”(50mm) thick LDS isolators molded to the following AASHTO bridge bearing specifications. All housings shall have 3/4”(20mm) minimum diameter jackscrews. Deflections shall not exceed 0.3”(7.5mm) nor the frequency 10Hz. Isolator shall be Mason Industries type FSN.

Table 1. AASHTO Bridge Bearing Specifications for polyisoprene

NOTE: 40 Durometer is not included in AASHTO Specifications. Numbers are Mason standard.

- In seismic zones double acting resilient cast in floating floor snubbers shall consist of a ductile iron housing locked into the floating floor. The housing shall have a removable cover plate to provide access to the adjustment of clearances in both the up and down directions of the resilient stops. Resilient stops shall be attached to a restraining bolt attached to the structural floor with an approved anchor. Double acting snubbers shall be Mason Industries Type SFFS.

BOND BREAKER MATERIAL

- Provide one (1) layer of 6 mil (0.15mm) polyethylene sheeting

PERIMETER ISOLATION

- Minimum 3/4”(20mm) thick PVC foam, density 7 lbs/ft3 average. PVC foam shall be Mason Industries P7.

- In seismic zone perimeter isolation shall be interspersed with 3/4”(20mm) thick, 60 durometer LDS bridge bearing pads the height of the perimeter material. Bridge bearing pad shall be made to the same AASHTO specifications, as shown for the FSN mountings and sized for a maximum deflection of 0.2”(5mm) at maximum earthquake forces. Interspersed pads shall be Mason Industries Type LDS-BBP.

PERIMETER CAULKING COMPOUND

- Non-hardening, drying or bleeding. Troweling or pouring grade. Caulking compound shall be Mason Industries Type CC-75.

FLOATING ROOF DRAINS

- Use standard roof drains cast into the floating roof. The structural floor shall have openings large enough to access pipe connections to the drains. Drain piping shall be suspended from combination spring and LDS hangers with a minimum of 1”(25mm) static deflection for 40 feet(12 meters) from the attachment point as shown on the drawings.

- Roof drains shall be (Architects Preference)

EXECUTION

INSTALLATION

- Install the floating roof systems according to the installation and adjustment procedures and drawings submitted by the isolator manufacturer and approved by the architect.

# JACK-UP SYSTEM SPECIFICATION

SPRING JACK-UP SYSTEM FOR TV STUDIOS, THEATRES, BOWLING ALLEYS, KITCHENS, SQUASH COURTS, EXERCISE ROOMS, ETC.

GENERAL

SCOPE

- Isolate floating floors from the building structure by means of jack-up spring isolators and perimeter isolation in each of the ______________ rooms as shown on the drawings. (Architect to fill in name of room.)

If sound barrier walls are used, add the following:

- Build sound barrier walls on the floating floors.

SUBSTITUTION OF MATERIALS

- Substitute materials shall meet or exceed the “quality” of the products which are listed in these Specifications. Submit samples for consideration on this project.

DESIGN

INTENT

- The floating floor system shall consist of a 4”(100mm) thick concrete slab isolated from and supported 2”(50mm) above the structural slab by resilient spring isolators within cast iron housings designed to jack up the floor after pouring on the sub-floor.

If sound barrier walls are used, add the following:

Sound barrier walls consisting of 6”(150mm) filled concrete block (Barrier wall construction may be changed by the architect when writing specification) shall rest on the floating floor with a 31/2”(90mm) air gap to the structural walls. (3”(90mm) may be reduced to 2”(50mm) if no sway braces are needed.)

- The floating floor slab shall be isolated from adjoining walls and curbs by means of perimeter isolation.

- Any floor drains, piping, conduit and duct penetrations must not short circuit the isolation system.

- In seismic zones the floating floor shall be restrained horizontally by curbs or walls designed to withstand the horizontal seismic forces. Solid bridge bearing LDS pads shall be interspersed between perimeter isolation to withstand the seismic forces with a maximum deflection of 0.2”(5mm). When perimeter cannot be used for seismic constraint, intersperse horizontal restraints within floor system.

PERFORMANCE REQUIREMENTS

- All spring isolators shall have the minimum specified deflection.

FLOOR SYSTEM CONSTRUCTION PROCEDURE

- The setting of all isolation materials and raising of the floor shall be performed by or under the supervision of the isolation manufacturer.

- Set and waterproof any drains and lower pipe seals in keeping with waterproofing specifications.

- Cement perimeter isolation around all walls, columns, curbs, etc.

  - In seismic zones intersperse the perimeter isolation with bridge bearing quality LDS pads the thickness of the perimeter isolation.

- Cover entire floor area with 6 mil (0.15mm) polyethylene sheeting and carry sheeting up perimeter isolation.

- Place spring isolator castings on a maximum of 54”(1370mm) centers in the general areas in strict accordance with the approved drawings prepared by the isolation manufacturer. Additional reinforcement such as in wall locations must be detailed on isolation manufacturer’s drawings when required. If sound barrier walls are used, add the following: Perimeter isolators shall be selected to support the wall weight in addition to the perimeter of the floating floor.

- Place reinforcing as shown on the drawings and pour floor monolithically.

- Raise floor 2”(50mm) by means of the isolator threaded sleeves and replace covers.

- Caulk perimeter isolation in all locations.

If sound barrier walls are used, add the following:

- Construct block walls on the floating floor being careful that mortar does not drop behind the walls. Place 2”(50mm) fiberglass bats against the structural wall as a precaution. Readjust perimeter isolators as required to compensate for wall weight as the wall is built. Provide sway braces and isolated angle iron wall braces at the top of the walls. Caulk angle iron braces.

SUBMITTALS

- Detailed product drawings including Load/Deflection curves of all isolators.

- Drawing or drawings showing:

  - Dead, live and concentrated loads.

  - Isolator sizes, deflections and locations.

If sound barrier walls are used, add the following to b:

Wall sway brace and isolated angle iron brace locations.

  - Any drain and penetration locations.

  - Size, type, elevation and spacing of concrete reinforcement.

  - Caulking details.

  - Floating floor and wall construction procedure.

QUALITY ASSURANCE

- Floating floor system components shall be designed and fabricated by a manufacturer with at least ten years experience in one hundred similar installations.

- The floating floor isolation materials shall be installed and the floor raised by or under the supervision of the isolator manufacturer.

SITE CONDITIONS

- If site conditions are unsatisfactory or raise questions about the installation of the floating floor, the work will not proceed until the condition has been corrected in a manner acceptable to the isolation manufacturer. The sub-floor must have the same pitch as the top of the floating floor or special provisions made for isolator housings of different height.

SEQUENCING AND SCHEDULING

- Coordinate work with other trades and coordinate scheduling with the construction supervisor to minimize delays.

PRODUCTS

ISOLATORS

- Casting or weldments consisting of an internally threaded outer housing complete with lugs to support the reinforcing system. The inner inverted cup shaped housing shall be externally threaded. The springs are compressed and the floor lifted by turns of the internal housing. Springs shall be seated in neoprene cups and housings shall have removable cover plates. Spring diameters shall be no less than 0.8 of the compressed height of the spring at rated load. Springs shall have a minimum additional travel to solid equal to 50% of the rated deflection. Spring deflections shall be a minimum of 0.75”(20mm). (Note to architect: Deflections may be changed as required.) Isolators shall be Mason Industries Type FS.

If sound barrier walls are used, add the following:

- Wall Sway Braces: Double acting LDS sway braces with a fail safe feature in three planes. Braces shall be furnished with a bracket for bolting to the structural wall and a hooked end for insertion in the masonry joint. Braces shall have a frequency not in excess of 10Hz based on the weight of the wall area per brace and a vertical stiffness not in excess of 50% of the horizontal. Sway Braces shall be Mason Industries Type DNSB.

- Angle Brackets: 11/2”(40mm) x 2”(50mm) angle iron sections with provision for bolting to the structure and a minimum thickness of 3/8”(9mm) sponge cemented to the vertical leg. Angle Brackets shall be Mason Industries Type AB-716.

BOND BREAKER MATERIAL

- Provide one (1) layer of 6 mil (0.15mm) polyethylene sheeting.

PERIMETER ISOLATION

- Minimum 3/4”(20mm) thick PVC foam, density 7 lbs/ft3 average. PVC foam shall be Mason Industries P7.

- In seismic zone perimeter isolation shall be interspersed with 3/4”(20mm) thick, 60 durometer LDS bridge bearing pads the height of the perimeter material. Bridge bearing pad shall be made to AASHTO specifications, as shown and sized for a maximum deflection of 0.2”(5mm) at maximum earthquake forces. Interspersed pads shall be Mason Industries Type LDS-BBP.

Table 1. AASHTO Bridge Bearing Specifications for polyisoprene

NOTE: 40 Durometer is not included in AASHTO Specifications. Numbers are Mason standard.

PERIMETER CAULKING COMPOUND

- Non-hardening, drying or bleeding. Troweling or pouring grade. Caulking compound shall be Mason Industries Type CC-75.

FLOATING FLOOR DRAINS

- Cast iron design. The upper funnel section cast into the floating floor. Lower bucket, built into the structure, shall retain water surrounding the upper section as a between floors sound seal. Weep holes are required to drain the structural floor. Floor drains shall have water proofing membrane clamps. Floor drains shall be Mason Industries Type CFD-18591.

EXECUTION

INSTALLATION

- Install the floating floor systems according to the installation and adjustment procedures and drawings submitted by the isolator manufacturer and approved by the architect.