SSLFH

SPECIFICATION

Equipment shall be installed on resilient mountings designed and rated to resist seismic forces in all directions. The snubber shall be adjustable in the vertical up direction and allow a maximum of 1/4” (6mm) travel in the vertical and horizontal direction before contacting the resilient snubbing collars. Mountings shall have an Anchorage Preapproval “OPA” Number from OSHPD in the state of California attesting to the minimum listed certified Horizontal and Vertical load ratings.

All mountings shall have adjusting bolts that are rigidly bolted to the equipment.

Spring diameters shall be no less than 0.8 of the compressed height of the spring at rated load. Springs shall have a minimum additional travel to solid equal to 50% of the rated deflection. Mountings shall have a minimum of 2 spring inspection ports. Submittals shall include spring diameters, deflections, and calculations signed by a registered engineer showing that the seismic loads the mountings are to resist have been properly calculated. Mountings shall be type SSLFH as manufactured by Mason Industries, Inc.

SAS or SASE

SPECIFICATION

Stud wedge anchors shall be manufactured from full diameter wire, not from undersized wire that is rolled to create the thread. The stud anchor shall also have a safety shoulder which fully supports the wedge ring under load. The stud anchor shall be zinc-coated steel for interior applications and stainless steel for exterior applications. The stud anchors shall have an evaluation report number from the ICC-ES verifying its allowable loads. Drill-in stud wedge anchors shall be type SAS or SASE as manufactured by Mason Industries, Inc.

SAST

SPECIFICATION

Screw type anchors are preferred in floor locations so anchors can be installed after isolators or equipment is in place. Anchors shall be manufactured from hardened steel and zinc electroplated for corrosion resistance. Screw type anchors shall have an evaluation report number from the ICC-ES verifying its allowable loads. Screw type anchors shall be type SAST as manufactured by Mason Industries, Inc.

SRA

SPECIFICATION

Adhesive type anchors shall include a two-component epoxy-based adhesive with zinc plated threaded anchor rods for interior application and stainless steel anchor rods for exterior application. The adhesive anchor shall have been tested and qualified for performance in cracked and un-cracked concrete per ICC-ES AC308. Anchors shall have an evaluation report from ICCES verifying allowable loads. Adhesive anchors shall be type SRA as manufactured by Mason Industries, Inc.

HPA

SPECIFICATION

Housekeeping pad anchors shall consist of a ductile iron casting that is tapered and hexagonal, smaller at its base than at its top. The upper portion shall have holes for rebar to pass through. The anchor shall be continuously threaded from top to bottom for the attachment of soleplates. Housekeeping pad anchors shall be attached to the structural slab using a stud wedge anchor. Housekeeping pad anchors shall be type HPA and stud wedge anchor shall be type SAS both as manufactured by Mason Industries, Inc.

Z-1225

SPECIFICATION

All-directional seismic snubbers shall consist of interlocking steel members restrained by a one-piece molded neoprene bushing of bridge bearing neoprene. Bushing shall be replaceable and a minimum of 1/4” (6mm) thick. Rated loadings shall not exceed 1000 psi (.7kg/mm2). A minimum air gap of 1/8” (3mm) shall be incorporated in the snubber design in all directions before contact is made between the rigid and resilient surfaces. Snubber end caps shall be removable to allow inspection of internal clearances. Neoprene bushings shall be rotated to insure no short circuits exist before systems are activated. Snubbers shall have an Anchorage Preapproval “OPA” Number from OSHPD in the State of California verifying the maximum certified horizontal and vertical load ratings. Snubber shall be type Z-1225 as manufactured by Mason Industries, Inc.

Z-1011

SPECIFICATION

All directional seismic snubbers shall consist of interlocking steel members restrained by shock absorbent rubber materials compounded to bridge bearing specifications. Elastomeric materials shall be replaceable and a minimum of 3/4” (19mm) thick. Rated loadings shall not exceed 1000 psi (.7kg/mm2). Snubbers shall be manufactured with an air gap between hard and resilient material of not less than 1/8” (3mm) or more than 1/4” (6mm). Snubbers shall be installed with factory set clearances. The capacity of the seismic snubber at 3/8” (9mm) deflection shall be equal or greater than the load assigned to the mounting grouping controlled by the snubber multiplied by the applicable “G” force. Submittals shall include the load deflection curves up to 1/2” (13mm) deflection in the x, y and z planes. Snubbers shall have an anchorage preapproval “OPA” number from OSHPD in the state of California verifying the maximum certified horizontal and vertical load ratings. Snubbers shall be type Z-1011 as manufactured by Mason Industries, Inc.